## general_data
Names | Values
building_quality | t_in floor_number 0 20 1 20 2 20 3 20
heating_syst | D
CP | RAD
t_in | 4000
n_50 | 6
U_wd | 1.5
U_sk | 2.5

## control_data
Names | Values
rh_table | F1
thermal_mass | H
infiltration_rate_setback | 0.5
time_setback_h | 14
time_reheat_h | 6
f_rh_min | 10

## materials_data
material | lambda | rho | c
concrete_bloc | 1.36 | 2000 | 1000
insulation | 0.026 | 80 | 840
reinforced_concrete | 2.3 | 2400 | 1000
concrete | 2.1 | 2400 | 1000
brick | 1.59 | 2200 | 1000
screed | 1.4 | 2000 | 1000
wood | 0.13 | 600 | 1600
foamglass | 0.055 | 150 | 1000
plaster_panel | 0.32 | 1200 | 1000
EPS_board | 0.034 | 25 | 1300
glass_wool | 0.036 | 28 | 1030
rock_wool | 0.035 | 115 | 1030
wood_wool | 0.039 | 48 | 2100
air_30mm_horizontal | 0.18 | 1.2 | 1000
air_40mm_horizontal | 0.24 | 1.2 | 1000
air_80mm_horizontal | 0.444 | 1.2 | 1000
wood_wool_complex | 0.046322 | 92.4138 | 2059.7701
rock_wool_complex | 0.04828 | 182.7957 | 1109.6774

## wall_types_layers_data
wall_type | layer | thickness | material
door_ext | 0 | 0.05 | wood
door_int | 0 | 0.005 | wood
door_int | 1 | 0.04 | air_40mm_horizontal
door_int | 2 | 0.005 | wood
floor_gr | 0 | 0.08 | concrete
floor_int | 0 | 0.3 | concrete
partition | 0 | 0.025 | plaster_panel
partition | 1 | 0.08 | air_80mm_horizontal
partition | 2 | 0.025 | plaster_panel
party_wall | 1 | 0.45 | brick
party_wall | 2 | 0.03 | air_30mm_horizontal
party_wall | 3 | 0.12 | wood_wool_complex
party_wall | 4 | 0.018 | wood
party_wall | 5 | 0.025 | plaster_panel
roof | 0 | 0.025 | plaster_panel
roof | 1 | 0.24 | rock_wool_complex
wall_brick | 0 | 0.45 | brick
wall_brick_isol | 0 | 0.025 | plaster_panel
wall_brick_isol | 1 | 0.03 | wood_wool_complex
wall_brick_isol | 2 | 0.24 | rock_wool_complex
wall_brick_isol | 3 | 0.018 | wood
wall_brick_isol | 4 | 0.45 | brick
wall_int | 0 | 0.19 | concrete_bloc

## wall_types_env_data
wall_type | thermal_bridges | external_clading | adjacent_entity | ground_contact
door_ext | TRUE | FALSE | FALSE | FALSE
door_int | FALSE | FALSE | FALSE | FALSE
floor_gr | FALSE | FALSE | FALSE | TRUE
floor_int | FALSE | FALSE | FALSE | FALSE
partition | FALSE | FALSE | FALSE | FALSE
party_wall | FALSE | FALSE | FALSE | FALSE
roof | TRUE | TRUE | FALSE | FALSE
wall_brick | FALSE | FALSE | FALSE | FALSE
wall_brick_isol | FALSE | FALSE | FALSE | FALSE
wall_int | FALSE | FALSE | FALSE | FALSE

## wall_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2 | interface_id
0 | 0 | wall_0 | wall |  | NE | -135 | 90 | 5.907 | 2.8 | 0 |  | 16.539 | 16.539
1 | 0 | wall_1 | wall |  | NW | 135 | 90 | 8.978 | 2.8 | 0 |  | 25.139 | 25.139
2 | 0 | wall_2 | wall |  | SW | 45 | 90 | 5.943 | 2.8 | 0 |  | 16.64 | 16.64
3 | 0 | wall_3 | wall |  | SE | -45 | 90 | 8.978 | 2.8 | 0 |  | 25.139 | 20.459
4 | 0 | floor | floor |  | S | 0 | 0 |  |  |  |  | 53.194 |  | ext_floor_0
5 | 0 | roof | roof |  | S | 0 | 180 |  |  |  |  | 53.194 | 53.194 | interface_0_1
6 | 0 | panel_3_0 | panel | wall_3 | SE | -45 | 90 | 0.8 | 2.1 | 0 | 2.149 | 1.68
7 | 0 | panel_3_1 | panel | wall_3 | SE | -45 | 90 | 0.8 | 2.1 | 0 | 5.373 | 1.68
8 | 1 | wall_0 | wall |  | NE | -135 | 90 | 6.262 | 4.5 | 0 |  | 28.177 | 28.177
9 | 1 | wall_1 | wall |  | SE | -45 | 90 | 3.131 | 4.5 | 0 |  | 14.089 | 12.199
10 | 1 | wall_2 | wall |  | NE | -135 | 90 | 8.185 | 4.5 | 0 |  | 36.834 | 34.314
11 | 1 | wall_3 | wall |  | NW | 135 | 90 | 12.146 | 4.5 | 0 |  | 54.657 | 41.157
12 | 1 | wall_4 | wall |  | SW | 45 | 90 | 14.447 | 4.5 | 0 |  | 65.011 | 47.131
13 | 1 | wall_5 | wall |  | SE | -45 | 90 | 9.015 | 4.5 | 0 |  | 40.568 | 36.968
14 | 1 | floor_1 | floor |  | S | 0 | 0 |  |  |  |  | 53.194 |  | interface_0_1
15 | 1 | floor_2 | floor |  | S | 0 | 0 |  |  |  |  | 102.811 |  | ext_floor_1
16 | 1 | roof_1 | roof |  | S | 0 | 180 |  |  |  |  | 153.388 | 156.005 | interface_1_2
17 | 1 | roof_2 | roof |  | S | 0 | 180 |  |  |  |  | 2.617 | 156.005 | ext_roof_1
18 | 1 | panel_1_0 | panel | wall_1 | SE | -45 | 90 | 0.9 | 2.1 | 0 | 1.547 | 1.89
19 | 1 | panel_2_0 | panel | wall_2 | NE | -135 | 90 | 1.2 | 2.1 | 0 | 0.293 | 2.52
20 | 1 | panel_3_0 | panel | wall_3 | NW | 135 | 90 | 3 | 4.5 | 0 | 0.214 | 13.5
21 | 1 | panel_4_0 | panel | wall_4 | SW | 45 | 90 | 1.2 | 2.4 | 0 | 6.755 | 2.88
22 | 2 | wall_0 | wall |  | NE | -135 | 90 | 6.646 | 4.34 | 0 |  | 28.843 | 26.239
23 | 2 | wall_1 | wall |  | SE | -45 | 90 | 3.021 | 4.34 | 0 |  | 13.111 | 11.221
24 | 2 | wall_2 | wall |  | NE | -135 | 90 | 7.753 | 4.34 | 0 |  | 33.65 | 21.49
25 | 2 | wall_3 | wall |  | NW | 135 | 90 | 12.033 | 4.34 | 0 |  | 52.223 | 39.203
26 | 2 | wall_4 | wall |  | SW | 45 | 90 | 14.433 | 4.34 | 0 |  | 62.639 | 46.439
27 | 2 | wall_5 | wall |  | SE | -45 | 90 | 8.995 | 4.34 | 0 |  | 39.04 | 35.44
28 | 2 | floor | floor |  | S | 0 | 0 |  |  |  |  | 153.388 |  | interface_1_2
29 | 2 | roof_1 | roof |  | S | 0 | 180 |  |  |  |  | 148.969 | 153.388 | interface_2_3
30 | 2 | roof_2 | roof |  | S | 0 | 180 |  |  |  |  | 4.419 | 153.388 | ext_roof_2
31 | 2 | panel_0_0 | panel | wall_0 | NE | -135 | 90 | 0.6 | 4.34 | 0 | 5.979 | 2.604
32 | 2 | panel_1_0 | panel | wall_1 | SE | -45 | 90 | 0.9 | 2.1 | 0 | 1.573 | 1.89
33 | 2 | panel_2_0 | panel | wall_2 | NE | -135 | 90 | 5.6 | 2 | 2.34 | 0.134 | 11.2
34 | 2 | panel_3_0 | panel | wall_3 | NW | 135 | 90 | 3 | 4.34 | 0 | 0.165 | 13.02
35 | 3 | wall_0 | wall |  | NE | -135 | 90 | 8.213 | 4.338 | 0 |  | 35.626 | 18.782
36 | 3 | wall_1 | wall |  | SE | -45 | 90 | 3.04 | 3.258 | 0 |  | 9.903 | 3.918
37 | 3 | wall_2 | wall |  | NE | -135 | 90 | 6.239 | 2.2 | 0 |  | 13.727 | 13.727
38 | 3 | wall_3 | wall |  | NW | 135 | 90 | 12.017 | 4.63 | 0 |  | 55.631 | 48.299
39 | 3 | wall_4 | wall |  | SW | 45 | 90 | 14.434 | 1.08 | 0 |  | 15.582 | 15.582
40 | 3 | wall_5 | wall |  | SE | -45 | 90 | 9.012 | 5.055 | 0 |  | 45.557 | 44.357
41 | 3 | floor | floor |  | S | 0 | 0 |  |  |  |  | 148.969 |  | interface_2_3
42 | 3 | roof_0 | roof |  | SW | 45 | 125.38 |  |  |  |  | 112.776 | 109.986 | ext_roof_3
43 | 3 | roof_1 | roof |  | NE | -135 | 145.16 |  |  |  |  | 101.95 | 94.81 | ext_roof_3
44 | 3 | panel_0_0 | panel | wall_0 | NE | -135 | 90 | 8.021 | 2.1 | 0 | 0.117 | 16.844
45 | 3 | panel_1_0 | panel | wall_1 | SE | -45 | 90 | 0.95 | 2.1 | 0 | 0.024 | 1.995
46 | 3 | panel_1_1 | panel | wall_1 | SE | -45 | 90 | 0.95 | 2.1 | 0 | 0.976 | 1.995
47 | 3 | panel_1_2 | panel | wall_1 | SE | -45 | 90 | 0.95 | 2.1 | 0 | 1.928 | 1.995
48 | 3 | panel_3_0 | panel | wall_3 | NW | 135 | 90 | 3.288 | 2.23 | 0 | 0.054 | 7.332

## windows_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2
5 | 0 | window_3_0 | window | wall_3 | SE | -45 | 90 | 1.1 | 1.2 | 0.9 | 6.582 | 1.32
16 | 1 | window_4_0 | window | wall_4 | SW | 45 | 90 | 2.4 | 3 | 0.6 | 10.22 | 7.2
17 | 1 | window_4_1 | window | wall_4 | SW | 45 | 90 | 1.2 | 3 | 0.6 | 3.512 | 3.6
18 | 1 | window_4_2 | window | wall_4 | SW | 45 | 90 | 1.2 | 2.3 | 1.3 | 1.465 | 2.76
20 | 1 | window_4_3 | window | wall_4 | SW | 45 | 90 | 1.2 | 1.2 | 2.4 | 6.737 | 1.44
22 | 1 | window_5_0 | window | wall_5 | SE | -45 | 90 | 0.6 | 3 | 0.6 | 1.603 | 1.8
23 | 1 | window_5_1 | window | wall_5 | SE | -45 | 90 | 0.6 | 3 | 0.6 | 6.699 | 1.8
31 | 2 | window_2_0 | window | wall_2 | NE | -135 | 90 | 0.8 | 1.2 | 0.9 | 5.801 | 0.96
36 | 2 | window_4_0 | window | wall_4 | SW | 45 | 90 | 0.6 | 3 | 0.6 | 1.773 | 1.8
37 | 2 | window_4_1 | window | wall_4 | SW | 45 | 90 | 1.2 | 3 | 0.6 | 3.495 | 3.6
38 | 2 | window_4_2 | window | wall_4 | SW | 45 | 90 | 1.2 | 3 | 0.6 | 7.221 | 3.6
39 | 2 | window_4_3 | window | wall_4 | SW | 45 | 90 | 2.4 | 3 | 0.6 | 10.229 | 7.2
41 | 2 | window_5_0 | window | wall_5 | SE | -45 | 90 | 0.6 | 3 | 0.6 | 1.605 | 1.8
42 | 2 | window_5_1 | window | wall_5 | SE | -45 | 90 | 0.6 | 3 | 0.6 | 6.761 | 1.8
56 | 3 | window_5_0 | window | wall_5 | SE | -45 | 90 | 0.6 | 1 | 0.7 | 1.658 | 0.6
57 | 3 | window_5_1 | window | wall_5 | SE | -45 | 90 | 0.6 | 1 | 0.7 | 6.702 | 0.6
60 | 3 | skylight_0 | skylight | roof_0 | SW | 45 | 125.38 | 0.931 | 1.559 | 3.586 | 2.466 | 1.451
61 | 3 | skylight_4 | skylight | roof_0 | SW | 45 | 125.38 | 0.475 | 0.878 | 1.734 | 9.725 | 0.417
62 | 3 | skylight_5 | skylight | roof_0 | SW | 45 | 125.38 | 0.514 | 0.81 | 1.773 | 6.776 | 0.416
63 | 3 | skylight_6 | skylight | roof_0 | SW | 45 | 125.38 | 0.534 | 0.946 | 1.7 | 2.744 | 0.505
65 | 3 | skylight_1 | skylight | roof_1 | NE | -135 | 145.16 | 0.893 | 0.983 | 6.201 | 10.991 | 0.878
66 | 3 | skylight_2 | skylight | roof_1 | NE | -135 | 145.16 | 1.993 | 2.48 | 6.252 | 4.957 | 4.944
67 | 3 | skylight_3 | skylight | roof_1 | NE | -135 | 145.16 | 1.025 | 1.287 | 0.996 | 1.831 | 1.319

## ventilation_data
floor_number | area_floor_m2 | ceiling_height_m | vol_int_m3 | q_su_m3h | q_ex_m3h | q_inf_m3h | q_infadd_m3h | q_gap_m3h | epsilon_rec | t_in_star | f_temp_v | H_V_su | H_V_ie | H_V
0 | 53.19 | 2.8 | 148.94 | 683.92 | 683.92 | 89.37 | 0 | 0 | 0.8 | 20 | 1 | 45.59 | 29.79 | 75.38
1 | 156 | 4.5 | 702.02 | 2005.78 | 2005.78 | 421.21 | 0 | 0 | 0.8 | 21.25 | 1.04 | 139.69 | 146.67 | 286.36
2 | 153.39 | 4.34 | 665.7 | 1972.13 | 1972.13 | 399.42 | 0 | 0 | 0.8 | 21.17 | 1.04 | 136.97 | 138.7 | 275.67
3 | 148.97 | 3.07 | 456.96 | 1915.32 | 1915.32 | 274.18 | 0 | 0 | 0.8 | 20 | 1 | 127.69 | 91.39 | 219.08

## walls_types
wall_type | thickness [m] | conductive resistance [m²K/W]
door_ext | 0.05 | 0.38
door_int | 0.05 | 0.24
floor_gr | 0.08 | 0.04
floor_int | 0.3 | 0.14
partition | 0.13 | 0.34
party_wall | 0.64 | 3.26
roof | 0.26 | 5.05
wall_brick | 0.45 | 0.28
wall_brick_isol | 0.76 | 6.12
wall_int | 0.19 | 0.14

## walls
| floor_number | type | azimuth_deg | slope_deg | wall_type | area [m²] | f_temp | U [W/m²K] | H_T [W/K] | PHI_T [W]
0 | 0 | wall | -135 | 90 | wall_brick | 17.9 | 0.75 | 2.21 | 29.7 | 832
1 | 0 | wall | 135 | 90 | wall_brick | 27.2 | 0.35714 | 2.21 | 21.5 | 603
2 | 0 | wall | 45 | 90 | wall_brick | 18.01 | 1 | 2.21 | 39.9 | 1117
3 | 0 | wall | -45 | 90 | wall_int | 22.14 | 0.75 | 3.24 | 53.9 | 1509
4 | 1 | wall | -135 | 90 | wall_brick | 31.93 | 0.79464 | 2.21 | 56.2 | 1574
5 | 1 | wall | -45 | 90 | partition | 13.83 | 0.79464 | 1.98 | 21.8 | 609
6 | 1 | wall | -135 | 90 | party_wall | 38.89 | 0.40179 | 0.29 | 4.6 | 128
7 | 1 | wall | 135 | 90 | wall_brick | 46.64 | 0.40179 | 2.21 | 41.5 | 1162
8 | 1 | wall | 45 | 90 | wall_brick | 53.42 | 1.0446 | 2.21 | 123.6 | 3460
9 | 1 | wall | -45 | 90 | wall_brick | 41.9 | 1.0446 | 2.21 | 96.9 | 2714
10 | 2 | wall | -135 | 90 | wall_brick | 28.96 | 0.79179 | 2.21 | 50.8 | 1422
11 | 2 | wall | -45 | 90 | partition | 12.38 | 0.79179 | 1.98 | 19.4 | 544
12 | 2 | wall | -135 | 90 | party_wall | 23.72 | 0.39893 | 0.29 | 2.8 | 77
13 | 2 | wall | 135 | 90 | wall_brick | 43.27 | 0.39893 | 2.21 | 38.2 | 1070
14 | 2 | wall | 45 | 90 | wall_brick | 51.25 | 1.0418 | 2.21 | 118.3 | 3311
15 | 2 | wall | -45 | 90 | wall_brick | 39.11 | 1.0418 | 2.21 | 90.3 | 2527
16 | 3 | wall | -135 | 90 | wall_brick | 20.58 | 1 | 2.21 | 45.6 | 1276
17 | 3 | wall | -45 | 90 | wall_brick | 4.42 | 1 | 2.21 | 9.8 | 274
18 | 3 | wall | -135 | 90 | roof | 16.32 | 1 | 0.19 | 4.7 | 132
19 | 3 | wall | 135 | 90 | wall_brick | 52.63 | 0.35714 | 2.21 | 41.6 | 1166
20 | 3 | wall | 45 | 90 | wall_brick_isol | 21.57 | 1 | 0.16 | 3.4 | 96
21 | 3 | wall | -45 | 90 | wall_brick_isol | 48 | 1 | 0.16 | 7.6 | 214
22 | 0 | panel | -45 | 90 | door_int | 1.68 | 0.75 | 2.43 | 3.1 | 86
23 | 0 | panel | -45 | 90 | door_int | 1.68 | 0.75 | 2.43 | 3.1 | 86
24 | 1 | panel | -45 | 90 | door_int | 1.89 | 0.75179 | 2.43 | 3.4 | 97
25 | 1 | panel | -135 | 90 | door_int | 2.52 | 0.35893 | 2.43 | 2.2 | 61
26 | 1 | panel | 135 | 90 | wall_brick | 13.5 | 1.0446 | 2.21 | 31.2 | 875
27 | 1 | panel | 45 | 90 | door_ext | 2.88 | 1.0071 | 1.81 | 5.5 | 155
28 | 2 | panel | -135 | 90 | partition | 2.6 | 0.79179 | 1.98 | 4.1 | 114
29 | 2 | panel | -45 | 90 | door_int | 1.89 | 0.75179 | 2.43 | 3.4 | 97
30 | 2 | panel | -135 | 90 | wall_brick | 11.2 | 1.0836 | 2.21 | 26.9 | 753
31 | 2 | panel | 135 | 90 | wall_brick | 13.02 | 1.0418 | 2.21 | 30 | 841
32 | 3 | panel | -135 | 90 | wall_brick | 16.84 | 0.75 | 2.21 | 28 | 783
33 | 3 | panel | -45 | 90 | wall_brick | 2 | 0.75 | 2.21 | 3.3 | 93
34 | 3 | panel | -45 | 90 | door_int | 2 | 0.75 | 2.43 | 3.6 | 102
35 | 3 | panel | -45 | 90 | wall_brick | 2 | 0.75 | 2.21 | 3.3 | 93
36 | 3 | panel | 135 | 90 | wall_brick | 7.33 | 1 | 2.21 | 16.2 | 455
37 | 0 | roof | 0 | 180 | floor_int | 53.19 | 0 | 3.21 | 0 | 0
38 | 1 | floor | 0 | 0 | floor_int | 53.19 | -0.035714 | 3.21 | -6.1 | -171
39 | 1 | roof | 0 | 180 | floor_int | 153.39 | 0.125 | 3.21 | 61.6 | 1724
40 | 2 | floor | 0 | 0 | floor_int | 153.39 | -0.035714 | 3.21 | -17.6 | -493
41 | 2 | roof | 0 | 180 | floor_int | 148.97 | 0.11929 | 3.21 | 57.1 | 1598
42 | 3 | floor | 0 | 0 | floor_int | 148.97 | 0 | 3.21 | 0 | 0
43 | 0 | floor | 0 | 0 | floor_gr | 53.19 | 0.35714 | 4.84 | 153.4 | 4294
44 | 1 | floor | 0 | 0 | floor_int | 102.81 | 0.71429 | 3.21 | 235.9 | 6605
45 | 1 | roof | 0 | 180 | floor_int | 2.62 | 0.875 | 3.21 | 7.4 | 206
46 | 2 | roof | 0 | 180 | floor_int | 4.42 | 0.86929 | 3.21 | 12.3 | 345
47 | 3 | roof | 45 | 125.38 | roof | 112.78 | 1 | 0.19 | 32.6 | 912
48 | 3 | roof | -135 | 145.16 | roof | 101.95 | 1 | 0.19 | 29.4 | 824
0 | 0 | window | -45 | 90 | window | 1.32 | 1 | 1.5 | 2.1 | 59
1 | 1 | window | 45 | 90 | window | 7.2 | 1.0393 | 1.5 | 12 | 335
2 | 1 | window | 45 | 90 | window | 3.6 | 1.0393 | 1.5 | 6 | 168
3 | 1 | window | 45 | 90 | window | 2.76 | 1.0518 | 1.5 | 4.6 | 130
4 | 1 | window | 45 | 90 | window | 1.44 | 1.0714 | 1.5 | 2.5 | 69
5 | 1 | window | -45 | 90 | window | 1.8 | 1.0393 | 1.5 | 3 | 84
6 | 1 | window | -45 | 90 | window | 1.8 | 1.0393 | 1.5 | 3 | 84
7 | 2 | window | -135 | 90 | window | 0.96 | 1.0179 | 1.5 | 1.6 | 44
8 | 2 | window | 45 | 90 | window | 1.8 | 1.0393 | 1.5 | 3 | 84
9 | 2 | window | 45 | 90 | window | 3.6 | 1.0393 | 1.5 | 6 | 168
10 | 2 | window | 45 | 90 | window | 3.6 | 1.0393 | 1.5 | 6 | 168
11 | 2 | window | 45 | 90 | window | 7.2 | 1.0393 | 1.5 | 12 | 335
12 | 2 | window | -45 | 90 | window | 1.8 | 1.0393 | 1.5 | 3 | 84
13 | 2 | window | -45 | 90 | window | 1.8 | 1.0393 | 1.5 | 3 | 84
14 | 3 | window | -45 | 90 | window | 0.6 | 1 | 1.5 | 1 | 27
15 | 3 | window | -45 | 90 | window | 0.6 | 1 | 1.5 | 1 | 27
16 | 3 | skylight | 45 | 125.38 | skylight | 1.45 | 1 | 2.5 | 3.8 | 106
17 | 3 | skylight | 45 | 125.38 | skylight | 0.42 | 1 | 2.5 | 1.1 | 30
18 | 3 | skylight | 45 | 125.38 | skylight | 0.42 | 1 | 2.5 | 1.1 | 30
19 | 3 | skylight | 45 | 125.38 | skylight | 0.5 | 1 | 2.5 | 1.3 | 37
20 | 3 | skylight | -135 | 145.16 | skylight | 0.88 | 1 | 2.5 | 2.3 | 64
21 | 3 | skylight | -135 | 145.16 | skylight | 4.94 | 1 | 2.5 | 12.9 | 360
22 | 3 | skylight | -135 | 145.16 | skylight | 1.32 | 1 | 2.5 | 3.4 | 96

## TR_by_walls_types_zone
floor_number | wall_type | area [m²] | H_T [W/K] | PHI_T [W]
0 | door_int | 3.36 | 6.1 | 171
0 | floor_gr | 53.19 | 153.4 | 4294
0 | floor_int | 53.19 | 0 | 0
0 | wall_brick | 63.11 | 91.1 | 2552
0 | wall_int | 22.14 | 53.9 | 1509
0 | window | 1.32 | 2.1 | 59
1 | door_ext | 2.88 | 5.5 | 155
1 | door_int | 4.41 | 5.6 | 158
1 | floor_int | 312.01 | 298.7 | 8364
1 | partition | 13.83 | 21.8 | 609
1 | party_wall | 38.89 | 4.6 | 128
1 | wall_brick | 187.39 | 349.5 | 9785
1 | window | 18.6 | 31.1 | 870
2 | door_int | 1.89 | 3.4 | 97
2 | floor_int | 306.78 | 51.8 | 1451
2 | partition | 14.99 | 23.5 | 658
2 | party_wall | 23.72 | 2.8 | 77
2 | wall_brick | 186.82 | 354.5 | 9925
2 | window | 20.76 | 34.5 | 966
3 | door_int | 2 | 3.6 | 102
3 | floor_int | 148.97 | 0 | 0
3 | roof | 231.04 | 66.7 | 1868
3 | skylight | 9.93 | 25.8 | 723
3 | wall_brick | 105.79 | 147.8 | 4140
3 | wall_brick_isol | 69.57 | 11.1 | 310
3 | window | 1.2 | 1.9 | 54

## TR_by_zone
floor_number | area_wv [m²] | area_wh [m²] | area_wd [m²] | area_T [m²] | H_T_wv [W/K] | H_T_wh [W/K] | H_T_wd [W/K] | H_T [W/K] | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W]
0 | 88.61 | 106.39 | 1.32 | 196.32 | 151.1 | 153.4 | 2.1 | 306.6 | 4232 | 4294 | 59 | 8585
1 | 247.4 | 312.01 | 18.6 | 578.01 | 387 | 298.7 | 31.1 | 716.7 | 10835 | 8364 | 870 | 20069
2 | 227.41 | 306.78 | 20.76 | 554.95 | 384.2 | 51.8 | 34.5 | 470.5 | 10757 | 1451 | 966 | 13173
3 | 193.67 | 363.7 | 11.13 | 568.49 | 167.2 | 62 | 27.7 | 257 | 4683 | 1736 | 777 | 7195

## PHI_by_zone
floor_number | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W] | PHI_V_su [W] | PHI_V_ie [W] | PHI_V [W] | PHI_TOT [W] | PHI_RH [W] | PHI_HL [W]
0 | 4232 | 4294 | 59 | 8585 | 1277 | 834 | 2111 | 10695 | 532 | 11227
1 | 10835 | 8364 | 870 | 20069 | 3911 | 4107 | 8018 | 28087 | 1560 | 29647
2 | 10757 | 1451 | 966 | 13173 | 3835 | 3884 | 7719 | 20892 | 1534 | 22426
3 | 4683 | 1736 | 777 | 7195 | 3575 | 2559 | 6134 | 13330 | 1490 | 14819

## PHI_by_facade
azimuth_deg | PHI_TOT [W] | PHI_HL [W]
-135 | 17850 | 19214
-45 | 19904 | 21230
45 | 18713 | 19819
135 | 16537 | 17857