## general_data
Names | Values
building_quality | t_in floor_number 0 20 1 17
heating_syst | B
CP | RAD
t_in | 4000
n_50 | 6
U_wd | 1.5
U_sk | 1.5

## control_data
Names | Values
rh_table | F1
thermal_mass | H
infiltration_rate_setback | 0.5
time_setback_h | 14
time_reheat_h | 6
f_rh_min | 10

## materials_data
material | lambda | rho | c
concrete_bloc | 1.36 | 2000 | 1000
insulation | 0.026 | 80 | 840
reinforced_concrete | 2.3 | 2400 | 1000
concrete | 2.1 | 2400 | 1000
brick | 1.59 | 2200 | 1000
screed | 1.4 | 2000 | 1000
wood | 0.13 | 600 | 1600
OSB | 0.12 | 553 | 1700
dwd_panel | 0.09 | 570 | 1700
foamglass | 0.055 | 150 | 1000
plaster_panel | 0.32 | 1200 | 1000
EPS_board | 0.034 | 25 | 1300
expanded_foam | 0.036 | 12 | 1300
PUR | 0.024 | 80 | 840
glass_wool | 0.036 | 28 | 1030
rock_wool | 0.035 | 115 | 1030
rock_wool_high_density | 0.04 | 150 | 1000
wood_wool | 0.039 | 48 | 2100
wood_fiber | 0.044 | 180 | 2100
roughcast | 1.3 | 1900 | 1000
tile | 0.7 | 2000 | 1000
linoleum | 0.17 | 1200 | 1400
air_30mm_horizontal | 0.18 | 1.2 | 1000
air_40mm_horizontal | 0.24 | 1.2 | 1000
air_80mm_horizontal | 0.444 | 1.2 | 1000
air_60mm_downward | 0.24 | 1.2 | 1000
wood_wool_complex | 0.046322 | 92.4138 | 2059.7701
rock_wool_complex | 0.04828 | 182.7957 | 1109.6774

## wall_types_layers_data
wall_type | layer | thickness | material
door_ext | 0 | 0.005 | wood
door_ext | 1 | 0.04 | PUR
door_ext | 2 | 0.005 | wood
door_int | 0 | 0.005 | wood
door_int | 1 | 0.04 | air_40mm_horizontal
door_int | 2 | 0.005 | wood
floor_ext | 0 | 0.003 | linoleum
floor_ext | 1 | 0.08 | screed
floor_ext | 2 | 0.02 | rock_wool_high_density
floor_ext | 3 | 0.018 | OSB
floor_ext | 4 | 0.24 | wood_wool_complex
floor_ext | 5 | 0.016 | dwd_panel
floor_ext | 6 | 0.05 | wood_fiber
floor_ext | 7 | 0.015 | roughcast
floor_gr | 0 | 0.05 | tile
floor_gr | 1 | 0.09 | screed
floor_gr | 2 | 0.15 | PUR
floor_gr | 3 | 0.12 | reinforced_concrete
floor_int | 0 | 0.003 | linoleum
floor_int | 1 | 0.08 | screed
floor_int | 2 | 0.02 | rock_wool_high_density
floor_int | 3 | 0.018 | OSB
floor_int | 4 | 0.1 | wood_wool_complex
floor_int | 5 | 0.015 | plaster_panel
partition | 0 | 0.025 | plaster_panel
partition | 1 | 0.08 | air_80mm_horizontal
partition | 2 | 0.025 | plaster_panel
party_wall | 0 | 0.025 | plaster_panel
party_wall | 1 | 0.018 | wood
party_wall | 2 | 0.12 | wood_wool_complex
party_wall | 3 | 0.03 | air_30mm_horizontal
party_wall | 4 | 0.45 | brick
roof | 0 | 0.025 | plaster_panel
roof | 1 | 0.24 | rock_wool_complex
roof | 2 | 0.018 | OSB
wall_ext_brick | 0 | 0.025 | plaster_panel
wall_ext_brick | 1 | 0.03 | wood_wool_complex
wall_ext_brick | 2 | 0.018 | OSB
wall_ext_brick | 3 | 0.018 | wood
wall_ext_brick | 4 | 0.24 | rock_wool_complex
wall_ext_brick | 5 | 0.016 | dwd_panel
wall_ext_gr | 0 | 0.025 | plaster_panel
wall_ext_gr | 1 | 0.018 | wood
wall_ext_gr | 2 | 0.12 | wood_wool_complex
wall_ext_gr | 3 | 0.04 | air_40mm_horizontal
wall_ext_gr | 4 | 0.45 | brick
wall_ext_roughcast | 0 | 0.025 | plaster_panel
wall_ext_roughcast | 1 | 0.03 | wood_wool_complex
wall_ext_roughcast | 2 | 0.018 | OSB
wall_ext_roughcast | 3 | 0.018 | wood
wall_ext_roughcast | 4 | 0.24 | rock_wool_complex
wall_ext_roughcast | 5 | 0.016 | dwd_panel
wall_ext_roughcast | 6 | 0.05 | wood_fiber
wall_ext_roughcast | 7 | 0.015 | roughcast
wall_int | 0 | 0.19 | brick

## wall_types_env_data
wall_type | thermal_bridges | external_clading | adjacent_entity | ground_contact
door_ext | FALSE | FALSE | FALSE | FALSE
door_int | FALSE | FALSE | FALSE | FALSE
floor_ext | FALSE | FALSE | FALSE | FALSE
floor_gr | FALSE | FALSE | FALSE | FALSE
floor_int | FALSE | FALSE | FALSE | FALSE
partition | FALSE | FALSE | FALSE | FALSE
party_wall | FALSE | FALSE | FALSE | FALSE
roof | FALSE | FALSE | FALSE | FALSE
wall_ext_brick | FALSE | FALSE | FALSE | FALSE
wall_ext_gr | FALSE | FALSE | FALSE | FALSE
wall_ext_roughcast | FALSE | FALSE | FALSE | FALSE
wall_int | FALSE | FALSE | FALSE | FALSE

## wall_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2 | interface_id
0 | 0 | wall_0 | wall |  | SE | -45 | 90 | 18.591 | 3.23 | 0 |  | 60.049 | 39.849
1 | 0 | wall_1 | wall |  | NE | -135 | 90 | 7.028 | 3.23 | 0 |  | 22.7 | 22.7
2 | 0 | wall_2 | wall |  | NW | 135 | 90 | 18.535 | 3.23 | 0 |  | 59.868 | 59.868
3 | 0 | wall_3 | wall |  | SW | 45 | 90 | 7.084 | 3.23 | 0 |  | 22.882 | 22.882
4 | 0 | floor | floor |  | S | 0 | 0 |  |  |  |  | 130.981 |  | ext_floor_0
5 | 0 | roof | roof |  | S | 0 | 180 |  |  |  |  | 130.981 |  | interface_0_1
6 | 0 | panel_0_0 | panel | wall_0 | SE | -45 | 90 | 1 | 2.1 | 0 | 9.751 | 2.1
7 | 0 | panel_0_1 | panel | wall_0 | SE | -45 | 90 | 1 | 2.1 | 0 | 16.011 | 2.1
8 | 0 | panel_0_2 | panel | wall_0 | SE | -45 | 90 | 1 | 2.1 | 0 | 11.682 | 2.1
9 | 1 | wall_0 | wall |  | NE | -135 | 90 | 11.018 | 5.748 | 0 |  | 63.331 | 47.543
10 | 1 | wall_1 | wall |  | NW | 135 | 90 | 18.684 | 4.666 | 0 |  | 87.187 | 43.472
11 | 1 | wall_2 | wall |  | SW | 45 | 90 | 11.001 | 5.75 | 0 |  | 63.255 | 60.735
12 | 1 | wall_3 | wall |  | SE | -45 | 90 | 18.736 | 4.63 | 0 |  | 86.741 | 76.533
13 | 1 | floor_1 | floor |  | S | 0 | 0 |  |  |  |  | 130.981 |  | interface_0_1
14 | 1 | floor_2 | floor |  | S | 0 | 0 |  |  |  |  | 75.004 |  | ext_floor_1
15 | 1 | roof_0 | roof |  | NW | 135 | 158.41 |  |  |  |  | 110.93 | 102.405 | ext_roof_1
16 | 1 | roof_1 | roof |  | SE | -45 | 157.99 |  |  |  |  | 110.926 | 110.926 | ext_roof_1
17 | 1 | panel_0_0 | panel | wall_0 | NE | -135 | 90 | 1.1 | 2.1 | 0 | 4.06 | 2.31
18 | 1 | panel_0_1 | panel | wall_0 | NE | -135 | 90 | 1.1 | 2.1 | 0 | 8.46 | 2.31
19 | 1 | panel_0_2 | panel | wall_0 | NE | -135 | 90 | 2.428 | 4.6 | 0 | 0.07 | 11.169
20 | 1 | panel_1_0 | panel | wall_1 | NW | 135 | 90 | 18.602 | 2.35 | 2.3 | 0.049 | 43.715
21 | 1 | panel_2_0 | panel | wall_2 | SW | 45 | 90 | 1.2 | 2.1 | 0 | 6.531 | 2.52

## windows_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2
0 | 0 | window_0_0 | window | wall_0 | SE | -45 | 90 | 3 | 2 | 0.4 | 1.03 | 6
1 | 0 | window_0_1 | window | wall_0 | SE | -45 | 90 | 1.5 | 2.4 | 0 | 4.46 | 3.6
2 | 0 | window_0_2 | window | wall_0 | SE | -45 | 90 | 0.5 | 2 | 0.4 | 7.612 | 1
5 | 0 | window_0_3 | window | wall_0 | SE | -45 | 90 | 0.5 | 2.1 | 0 | 9.214 | 1.05
6 | 0 | window_0_4 | window | wall_0 | SE | -45 | 90 | 0.5 | 2.1 | 0 | 17.029 | 1.05
7 | 0 | window_0_5 | window | wall_0 | SE | -45 | 90 | 1 | 0.3 | 2.1 | 11.654 | 0.3
8 | 0 | window_0_6 | window | wall_0 | SE | -45 | 90 | 1.5 | 0.3 | 2.1 | 16.014 | 0.45
10 | 0 | window_0_7 | window | wall_0 | SE | -45 | 90 | 1.5 | 0.3 | 2.1 | 9.273 | 0.45
25 | 1 | window_3_0 | window | wall_3 | SE | -45 | 90 | 0.8 | 3.19 | 0.9 | 1.335 | 2.552
26 | 1 | window_3_1 | window | wall_3 | SE | -45 | 90 | 0.8 | 3.19 | 0.9 | 3.335 | 2.552
27 | 1 | window_3_2 | window | wall_3 | SE | -45 | 90 | 0.8 | 3.19 | 0.9 | 5.335 | 2.552
28 | 1 | window_3_3 | window | wall_3 | SE | -45 | 90 | 0.8 | 3.19 | 0.9 | 7.335 | 2.552
31 | 1 | skylight_0 | skylight | roof_0 | NW | 135 | 158.41 | 9.052 | 0.942 | 4.948 | 6.182 | 8.525

## ventilation_data
floor_number | area_floor_m2 | ceiling_height_m | vol_int_m3 | q_su_m3h | q_ex_m3h | q_inf_m3h | q_infadd_m3h | q_gap_m3h | epsilon_rec | t_in_star | f_temp_v | H_V_su | H_V_ie | H_V
0 | 130.98 | 3.23 | 423.07 | 1684.04 | 1684.04 | 253.84 | 0 | 0 | 0.8 | 20 | 1 | 112.27 | 84.61 | 196.88
1 | 205.98 | 5.19 | 1069.06 | 2648.38 | 2648.38 | 641.44 | 0 | 0 | 0.8 | 18.6 | 1.06 | 187.82 | 227.45 | 415.28

## walls_types
wall_type | thickness [m] | conductive resistance [m²K/W]
door_ext | 0.05 | 1.74
door_int | 0.05 | 0.24
floor_ext | 0.44 | 7.23
floor_gr | 0.41 | 6.44
floor_int | 0.24 | 2.93
partition | 0.13 | 0.34
party_wall | 0.64 | 3.26
roof | 0.28 | 5.2
wall_ext_brick | 0.35 | 6.16
wall_ext_gr | 0.65 | 3.26
wall_ext_roughcast | 0.41 | 7.31
wall_int | 0.19 | 0.12

## walls
| floor_number | type | azimuth_deg | slope_deg | wall_type | area [m²] | f_temp | U [W/m²K] | H_T [W/K] | PHI_T [W]
0 | 0 | wall | -45 | 90 | wall_ext_brick | 46.36 | 1 | 0.16 | 7.3 | 205
1 | 0 | wall | -135 | 90 | party_wall | 26.41 | 0.35714 | 0.29 | 2.8 | 77
2 | 0 | wall | 135 | 90 | wall_ext_gr | 69.65 | 1 | 0.29 | 20.3 | 569
3 | 0 | wall | 45 | 90 | party_wall | 26.62 | 0.35714 | 0.29 | 2.8 | 78
4 | 1 | wall | -135 | 90 | party_wall | 53.54 | 0.35496 | 0.29 | 5.5 | 139
5 | 1 | wall | 135 | 90 | wall_ext_gr | 50.23 | 1.0533 | 0.29 | 15.4 | 386
6 | 1 | wall | 45 | 90 | party_wall | 68.39 | 0.355 | 0.29 | 7.1 | 177
7 | 1 | wall | -45 | 90 | wall_ext_roughcast | 88.52 | 1.0526 | 0.13 | 12.5 | 311
8 | 0 | panel | -45 | 90 | door_ext | 2.1 | 1 | 0.52 | 1.1 | 31
9 | 0 | panel | -45 | 90 | door_ext | 2.1 | 1 | 0.52 | 1.1 | 31
10 | 0 | panel | -45 | 90 | door_ext | 2.1 | 1 | 0.52 | 1.1 | 31
11 | 1 | panel | -135 | 90 | door_int | 2.31 | 0.282 | 2.43 | 1.6 | 40
12 | 1 | panel | -135 | 90 | door_int | 2.31 | 0.282 | 2.43 | 1.6 | 40
13 | 1 | panel | -135 | 90 | wall_ext_roughcast | 11.17 | 1.052 | 0.13 | 1.6 | 39
14 | 1 | panel | 135 | 90 | wall_ext_brick | 43.72 | 1.099 | 0.16 | 7.6 | 190
15 | 1 | panel | 45 | 90 | door_int | 2.52 | 0.282 | 2.43 | 1.7 | 43
16 | 0 | roof | 0 | 180 | floor_int | 130.98 | 0.10714 | 0.32 | 4.5 | 127
17 | 1 | floor | 0 | 0 | floor_int | 130.98 | -0.16 | 0.32 | -6.8 | -169
18 | 0 | floor | 0 | 0 | floor_gr | 130.98 | 0.35714 | 0.15 | 7.1 | 198
19 | 1 | floor | 0 | 0 | floor_ext | 75 | 0.96 | 0.14 | 9.7 | 243
20 | 1 | roof | 135 | 158.41 | roof | 110.93 | 1.1676 | 0.19 | 24.1 | 603
21 | 1 | roof | -45 | 157.99 | roof | 110.93 | 1.1676 | 0.19 | 24.1 | 603
0 | 0 | window | -45 | 90 | window | 6 | 1 | 1.5 | 9.3 | 260
1 | 0 | window | -45 | 90 | window | 3.6 | 1 | 1.5 | 5.6 | 156
2 | 0 | window | -45 | 90 | window | 1 | 1 | 1.5 | 1.6 | 43
3 | 0 | window | -45 | 90 | window | 1.05 | 1 | 1.5 | 1.6 | 46
4 | 0 | window | -45 | 90 | window | 1.05 | 1 | 1.5 | 1.6 | 46
5 | 0 | window | -45 | 90 | window | 0.3 | 1 | 1.5 | 0.5 | 13
6 | 0 | window | -45 | 90 | window | 0.45 | 1 | 1.5 | 0.7 | 20
7 | 0 | window | -45 | 90 | window | 0.45 | 1 | 1.5 | 0.7 | 20
8 | 1 | window | -45 | 90 | window | 2.55 | 1.0598 | 1.5 | 4.2 | 105
9 | 1 | window | -45 | 90 | window | 2.55 | 1.0598 | 1.5 | 4.2 | 105
10 | 1 | window | -45 | 90 | window | 2.55 | 1.0598 | 1.5 | 4.2 | 105
11 | 1 | window | -45 | 90 | window | 2.55 | 1.0598 | 1.5 | 4.2 | 105
12 | 1 | skylight | 135 | 158.41 | skylight | 8.52 | 1.225 | 1.5 | 16.2 | 405

## TR_by_walls_types_zone
floor_number | wall_type | area [m²] | H_T [W/K] | PHI_T [W]
0 | door_ext | 6.3 | 3.3 | 92
0 | floor_gr | 130.98 | 7.1 | 198
0 | floor_int | 130.98 | 4.5 | 127
0 | party_wall | 53.03 | 5.5 | 155
0 | wall_ext_brick | 46.36 | 7.3 | 205
0 | wall_ext_gr | 69.65 | 20.3 | 569
0 | window | 13.9 | 21.5 | 603
1 | door_int | 7.14 | 4.9 | 122
1 | floor_ext | 75 | 9.7 | 243
1 | floor_int | 130.98 | -6.8 | -169
1 | party_wall | 121.93 | 12.6 | 316
1 | roof | 221.86 | 48.3 | 1206
1 | skylight | 8.52 | 16.2 | 405
1 | wall_ext_brick | 43.72 | 7.6 | 190
1 | wall_ext_gr | 50.23 | 15.4 | 386
1 | wall_ext_roughcast | 99.69 | 14 | 351
1 | window | 10.21 | 16.8 | 419

## TR_by_zone
floor_number | area_wv [m²] | area_wh [m²] | area_wd [m²] | area_T [m²] | H_T_wv [W/K] | H_T_wh [W/K] | H_T_wd [W/K] | H_T [W/K] | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W]
0 | 175.35 | 261.96 | 13.9 | 451.21 | 36.5 | 11.6 | 21.5 | 69.6 | 1021 | 325 | 603 | 1950
1 | 322.7 | 427.84 | 18.73 | 769.27 | 54.6 | 51.2 | 33 | 138.8 | 1365 | 1281 | 824 | 3469

## PHI_by_zone
floor_number | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W] | PHI_V_su [W] | PHI_V_ie [W] | PHI_V [W] | PHI_TOT [W] | PHI_RH [W] | PHI_HL [W]
0 | 1021 | 325 | 603 | 1950 | 3144 | 2369 | 5513 | 7463 | 1310 | 8772
1 | 1365 | 1281 | 824 | 3469 | 4696 | 5686 | 10382 | 13851 | 2060 | 15911

## PHI_by_facade
azimuth_deg | PHI_TOT [W] | PHI_HL [W]
-135 | 3662 | 4274
-45 | 7263 | 8335
45 | 3690 | 4313
135 | 6699 | 7762