## general_data
Names | Values
building_quality | t_in floor_number 0 20 1 20 2 20 3 20 4 20 5 20
heating_syst | A
CP | RAD
t_in | 1000
n_50 | 1
U_wd | 1.05
U_sk | 1.5

## control_data
Names | Values
rh_table | F1
thermal_mass | H
infiltration_rate_setback | 0.5
time_setback_h | 14
time_reheat_h | 6
f_rh_min | 10

## materials_data
| material | lambda | rho | c
0 | concrete_bloc | 1.36 | 2000 | 1000
1 | insulation | 0.026 | 80 | 840
2 | reinforced_concrete | 2.3 | 2400 | 1000
3 | concrete | 2.1 | 2400 | 1000
4 | brick | 1.59 | 2200 | 1000
5 | screed | 1.4 | 2000 | 1000
6 | foamglass | 0.055 | 150 | 1000
7 | plaster_panel | 0.32 | 1200 | 1000
8 | EPS_board | 0.034 | 25 | 1300

## wall_types_layers_data
wall_type | layer | thickness | material
floor_ext | 0 | 0.07 | screed
floor_ext | 1 | 0.4 | concrete
floor_gr | 0 | 0.07 | screed
floor_gr | 1 | 0.3 | concrete
floor_gr | 2 | 0.1 | foamglass
floor_sep_i | 0 | 0.075 | screed
floor_sep_i | 1 | 0.05 | insulation
floor_sep_i | 2 | 0.3 | concrete
floor_sep_u | 0 | 0.06 | screed
floor_sep_u | 1 | 0.065 | insulation
floor_sep_u | 2 | 0.3 | concrete
roof | 0 | 0.3 | reinforced_concrete
roof | 1 | 0.3 | insulation
roof_terrace | 0 | 0.3 | reinforced_concrete
roof_terrace | 1 | 0.2 | insulation
transom | 0 | 0.01 | plaster_panel
transom | 0 | 0.1 | EPS_board
wall_ext | 0 | 0.19 | concrete_bloc
wall_ext | 1 | 0.1 | insulation
wall_sep | 0 | 0.19 | concrete_bloc

## wall_types_env_data
wall_type | thermal_bridges | external_clading | adjacent_entity | ground_contact
floor_ext | TRUE | FALSE | FALSE | FALSE
floor_gr | FALSE | FALSE | FALSE | TRUE
floor_sep_i | FALSE | FALSE | FALSE | FALSE
floor_sep_u | FALSE | FALSE | FALSE | FALSE
roof | TRUE | FALSE | FALSE | FALSE
roof_terrace | TRUE | FALSE | FALSE | FALSE
transom | TRUE | FALSE | FALSE | FALSE
wall_ext | TRUE | TRUE | FALSE | FALSE
wall_sep | FALSE | FALSE | FALSE | FALSE

## wall_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2 | interface_id
0 | 0 | wall_0 | wall |  | E | -90 | 90 | 1.635 | 3.01 | 0 |  | 4.921 | 4.921
1 | 0 | wall_1 | wall |  | N | 180 | 90 | 11.661 | 3.01 | 0 |  | 35.101 | 20.221
2 | 0 | wall_2 | wall |  | W | 90 | 90 | 27.519 | 3.01 | 0 |  | 82.833 | 54.033
3 | 0 | wall_3 | wall |  | S | 0 | 90 | 11.661 | 3.01 | 0 |  | 35.101 | 23.581
4 | 0 | wall_4 | wall |  | E | -90 | 90 | 3.491 | 3.01 | 0 |  | 10.507 | 8.587
5 | 0 | wall_5 | wall |  | S | 0 | 90 | 1.064 | 3.01 | 0 |  | 3.202 | 0.802
6 | 0 | wall_6 | wall |  | E | -90 | 90 | 22.263 | 3.01 | 0 |  | 67.011 | 7.941
7 | 0 | wall_7 | wall |  | N | 180 | 90 | 1.193 | 3.01 | 0 |  | 3.592 | 3.592
8 | 0 | floor | floor |  | S | 0 | 0 |  |  |  |  | 347.82 |  | ext_floor_0
9 | 0 | roof | roof |  | S | 0 | 180 |  |  |  |  | 347.82 |  | interface_0_1
10 | 0 | panel_6_0 | panel | wall_6 | E | -90 | 90 | 5.1 | 2.2 | 0 | 17.026 | 11.22
11 | 0 | panel_6_1 | panel | wall_6 | E | -90 | 90 | 16.5 | 0.5 | 2.4 | 0.099 | 8.25
12 | 1 | wall_0 | wall |  | N | 180 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
13 | 1 | wall_1 | wall |  | E | -90 | 90 | 1.769 | 3.01 | 0 |  | 5.323 | 5.323
14 | 1 | wall_2 | wall |  | N | 180 | 90 | 11.585 | 3.01 | 0 |  | 34.87 | 23.35
15 | 1 | wall_3 | wall |  | W | 90 | 90 | 27.457 | 3.01 | 0 |  | 82.645 | 53.845
16 | 1 | wall_4 | wall |  | S | 0 | 90 | 11.497 | 3.01 | 0 |  | 34.605 | 23.085
17 | 1 | wall_5 | wall |  | E | -90 | 90 | 3.449 | 3.01 | 0 |  | 10.381 | 8.461
18 | 1 | wall_6 | wall |  | S | 0 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
19 | 1 | wall_7 | wall |  | E | -90 | 90 | 22.285 | 3.01 | 0 |  | 67.076 | 59.156
20 | 1 | floor_1 | floor |  | S | 0 | 0 |  |  |  |  | 347.82 |  | interface_0_1
21 | 1 | floor_2 | floor |  | S | 0 | 0 |  |  |  |  | 2.165 |  | ext_floor_1
22 | 1 | roof | roof |  | S | 0 | 180 |  |  |  |  | 349.985 |  | interface_1_2
23 | 2 | wall_0 | wall |  | N | 180 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
24 | 2 | wall_1 | wall |  | E | -90 | 90 | 1.769 | 3.01 | 0 |  | 5.323 | 5.323
25 | 2 | wall_2 | wall |  | N | 180 | 90 | 11.585 | 3.01 | 0 |  | 34.87 | 23.35
26 | 2 | wall_3 | wall |  | W | 90 | 90 | 27.457 | 3.01 | 0 |  | 82.645 | 53.845
27 | 2 | wall_4 | wall |  | S | 0 | 90 | 11.497 | 3.01 | 0 |  | 34.605 | 23.085
28 | 2 | wall_5 | wall |  | E | -90 | 90 | 3.449 | 3.01 | 0 |  | 10.381 | 8.461
29 | 2 | wall_6 | wall |  | S | 0 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
30 | 2 | wall_7 | wall |  | E | -90 | 90 | 22.285 | 3.01 | 0 |  | 67.076 | 59.156
31 | 2 | floor | floor |  | S | 0 | 0 |  |  |  |  | 349.985 |  | interface_1_2
32 | 2 | roof | roof |  | S | 0 | 180 |  |  |  |  | 349.985 |  | interface_2_3
33 | 3 | wall_0 | wall |  | N | 180 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
34 | 3 | wall_1 | wall |  | E | -90 | 90 | 1.769 | 3.01 | 0 |  | 5.323 | 5.323
35 | 3 | wall_2 | wall |  | N | 180 | 90 | 11.585 | 3.01 | 0 |  | 34.87 | 23.35
36 | 3 | wall_3 | wall |  | W | 90 | 90 | 27.457 | 3.01 | 0 |  | 82.645 | 53.845
37 | 3 | wall_4 | wall |  | S | 0 | 90 | 11.497 | 3.01 | 0 |  | 34.605 | 23.085
38 | 3 | wall_5 | wall |  | E | -90 | 90 | 3.449 | 3.01 | 0 |  | 10.381 | 8.461
39 | 3 | wall_6 | wall |  | S | 0 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
40 | 3 | wall_7 | wall |  | E | -90 | 90 | 22.285 | 3.01 | 0 |  | 67.076 | 59.156
41 | 3 | floor | floor |  | S | 0 | 0 |  |  |  |  | 349.985 |  | interface_2_3
42 | 3 | roof | roof |  | S | 0 | 180 |  |  |  |  | 349.985 |  | interface_3_4
43 | 4 | wall_0 | wall |  | N | 180 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
44 | 4 | wall_1 | wall |  | E | -90 | 90 | 1.769 | 3.01 | 0 |  | 5.323 | 5.323
45 | 4 | wall_2 | wall |  | N | 180 | 90 | 11.585 | 3.01 | 0 |  | 34.87 | 23.35
46 | 4 | wall_3 | wall |  | W | 90 | 90 | 27.457 | 3.01 | 0 |  | 82.645 | 53.845
47 | 4 | wall_4 | wall |  | S | 0 | 90 | 11.497 | 3.01 | 0 |  | 34.605 | 23.085
48 | 4 | wall_5 | wall |  | E | -90 | 90 | 3.449 | 3.01 | 0 |  | 10.381 | 8.461
49 | 4 | wall_6 | wall |  | S | 0 | 90 | 1.459 | 3.01 | 0 |  | 4.392 | 0.78
50 | 4 | wall_7 | wall |  | E | -90 | 90 | 22.285 | 3.01 | 0 |  | 67.076 | 59.156
51 | 4 | floor | floor |  | S | 0 | 0 |  |  |  |  | 349.985 |  | interface_3_4
52 | 4 | roof_1 | roof |  | S | 0 | 180 |  |  |  |  | 266.365 |  | interface_4_5
53 | 4 | roof_2 | roof |  | S | 0 | 180 |  |  |  |  | 83.62 |  | ext_roof_4
54 | 5 | wall_0 | wall |  | W | 90 | 90 | 22.367 | 3.01 | 0 |  | 67.324 | 1.104
55 | 5 | wall_1 | wall |  | S | 0 | 90 | 11.908 | 3.01 | 0 |  | 35.842 | 1.528
56 | 5 | wall_2 | wall |  | E | -90 | 90 | 22.446 | 3.01 | 0 |  | 67.561 | 59.641
57 | 5 | wall_3 | wall |  | N | 180 | 90 | 11.869 | 3.01 | 0 |  | 35.725 | 1.411
58 | 5 | floor | floor |  | S | 0 | 0 |  |  |  |  | 266.365 |  | interface_4_5
59 | 5 | roof | roof |  | S | 0 | 180 |  |  |  |  | 266.365 |  | ext_roof_5

## windows_data
| floor_number | id | type | parent | orientation | azimuth_deg | slope_deg | width_m | height_m | sill_height_m | dist_corner_m | area_m2 | net_area_m2
1 | 0 | window_1_0 | window | wall_1 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 7.887 | 1.92
2 | 0 | window_1_1 | window | wall_1 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 9.687 | 1.92
3 | 0 | window_1_2 | window | wall_1 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 0.709 | 1.92
4 | 0 | window_1_3 | window | wall_1 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 2.509 | 1.92
5 | 0 | window_1_4 | window | wall_1 | N | 180 | 90 | 3 | 2.4 | 0 | 4.212 | 7.2
7 | 0 | window_2_0 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 0.582 | 1.92
8 | 0 | window_2_1 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 2.382 | 1.92
9 | 0 | window_2_2 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 4.182 | 1.92
10 | 0 | window_2_3 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 5.982 | 1.92
11 | 0 | window_2_4 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 7.782 | 1.92
12 | 0 | window_2_5 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 9.582 | 1.92
13 | 0 | window_2_6 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 11.382 | 1.92
14 | 0 | window_2_7 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 13.182 | 1.92
15 | 0 | window_2_8 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 14.982 | 1.92
16 | 0 | window_2_9 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 16.782 | 1.92
17 | 0 | window_2_10 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 18.582 | 1.92
18 | 0 | window_2_11 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 20.382 | 1.92
19 | 0 | window_2_12 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 22.182 | 1.92
20 | 0 | window_2_13 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 23.982 | 1.92
21 | 0 | window_2_14 | window | wall_2 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 25.782 | 1.92
23 | 0 | window_3_0 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 0.819 | 1.92
24 | 0 | window_3_1 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 2.619 | 1.92
25 | 0 | window_3_2 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 4.419 | 1.92
26 | 0 | window_3_3 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 6.219 | 1.92
27 | 0 | window_3_4 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 8.019 | 1.92
28 | 0 | window_3_5 | window | wall_3 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 9.819 | 1.92
30 | 0 | window_4_0 | window | wall_4 | E | -90 | 90 | 1.2 | 1.6 | 0.8 | 0.525 | 1.92
32 | 0 | window_5_0 | window | wall_5 | S | 0 | 90 | 1 | 2.4 | 0 | 0.032 | 2.4
34 | 0 | window_6_0 | window | wall_6 | E | -90 | 90 | 16.5 | 2.4 | 0 | 0.035 | 39.6
41 | 1 | window_0_0 | window | wall_0 | N | 180 | 90 | 1.2 | 3.01 | 0 | 0.233 | 3.612
44 | 1 | window_2_0 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 0.743 | 1.92
45 | 1 | window_2_1 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 2.543 | 1.92
46 | 1 | window_2_2 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 4.343 | 1.92
47 | 1 | window_2_3 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 6.143 | 1.92
48 | 1 | window_2_4 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 7.943 | 1.92
49 | 1 | window_2_5 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 9.743 | 1.92
51 | 1 | window_3_0 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 0.482 | 1.92
52 | 1 | window_3_1 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 2.282 | 1.92
53 | 1 | window_3_2 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 4.082 | 1.92
54 | 1 | window_3_3 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 5.882 | 1.92
55 | 1 | window_3_4 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 7.682 | 1.92
56 | 1 | window_3_5 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 9.482 | 1.92
57 | 1 | window_3_6 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 11.282 | 1.92
58 | 1 | window_3_7 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 13.082 | 1.92
59 | 1 | window_3_8 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 14.882 | 1.92
60 | 1 | window_3_9 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 16.682 | 1.92
61 | 1 | window_3_10 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 18.482 | 1.92
62 | 1 | window_3_11 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 20.282 | 1.92
63 | 1 | window_3_12 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 22.082 | 1.92
64 | 1 | window_3_13 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 23.882 | 1.92
65 | 1 | window_3_14 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 25.682 | 1.92
67 | 1 | window_4_0 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 0.617 | 1.92
68 | 1 | window_4_1 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 2.417 | 1.92
69 | 1 | window_4_2 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 4.217 | 1.92
70 | 1 | window_4_3 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 6.017 | 1.92
71 | 1 | window_4_4 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 7.817 | 1.92
72 | 1 | window_4_5 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 9.617 | 1.92
74 | 1 | window_5_0 | window | wall_5 | E | -90 | 90 | 1.2 | 1.6 | 0.8 | 0.526 | 1.92
76 | 1 | window_6_0 | window | wall_6 | S | 0 | 90 | 1.2 | 3.01 | 0 | 0 | 3.612
78 | 1 | window_7_0 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 1.284 | 1.44
79 | 1 | window_7_1 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 4.884 | 1.44
80 | 1 | window_7_2 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 8.484 | 1.44
81 | 1 | window_7_3 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 12.084 | 1.44
82 | 1 | window_7_4 | window | wall_7 | E | -90 | 90 | 0.9 | 0.8 | 0.8 | 15.782 | 0.72
83 | 1 | window_7_5 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 19.375 | 1.44
87 | 2 | window_0_0 | window | wall_0 | N | 180 | 90 | 1.2 | 3.01 | 0 | 0.233 | 3.612
90 | 2 | window_2_0 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 0.743 | 1.92
91 | 2 | window_2_1 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 2.543 | 1.92
92 | 2 | window_2_2 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 4.343 | 1.92
93 | 2 | window_2_3 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 6.143 | 1.92
94 | 2 | window_2_4 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 7.943 | 1.92
95 | 2 | window_2_5 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 9.743 | 1.92
97 | 2 | window_3_0 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 0.482 | 1.92
98 | 2 | window_3_1 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 2.282 | 1.92
99 | 2 | window_3_2 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 4.082 | 1.92
100 | 2 | window_3_3 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 5.882 | 1.92
101 | 2 | window_3_4 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 7.682 | 1.92
102 | 2 | window_3_5 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 9.482 | 1.92
103 | 2 | window_3_6 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 11.282 | 1.92
104 | 2 | window_3_7 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 13.082 | 1.92
105 | 2 | window_3_8 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 14.882 | 1.92
106 | 2 | window_3_9 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 16.682 | 1.92
107 | 2 | window_3_10 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 18.482 | 1.92
108 | 2 | window_3_11 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 20.282 | 1.92
109 | 2 | window_3_12 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 22.082 | 1.92
110 | 2 | window_3_13 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 23.882 | 1.92
111 | 2 | window_3_14 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 25.682 | 1.92
113 | 2 | window_4_0 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 0.617 | 1.92
114 | 2 | window_4_1 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 2.417 | 1.92
115 | 2 | window_4_2 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 4.217 | 1.92
116 | 2 | window_4_3 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 6.017 | 1.92
117 | 2 | window_4_4 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 7.817 | 1.92
118 | 2 | window_4_5 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 9.617 | 1.92
120 | 2 | window_5_0 | window | wall_5 | E | -90 | 90 | 1.2 | 1.6 | 0.8 | 0.526 | 1.92
122 | 2 | window_6_0 | window | wall_6 | S | 0 | 90 | 1.2 | 3.01 | 0 | 0 | 3.612
124 | 2 | window_7_0 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 1.284 | 1.44
125 | 2 | window_7_1 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 4.884 | 1.44
126 | 2 | window_7_2 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 8.484 | 1.44
127 | 2 | window_7_3 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 12.084 | 1.44
128 | 2 | window_7_4 | window | wall_7 | E | -90 | 90 | 0.9 | 0.8 | 0.8 | 15.782 | 0.72
129 | 2 | window_7_5 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 19.375 | 1.44
133 | 3 | window_0_0 | window | wall_0 | N | 180 | 90 | 1.2 | 3.01 | 0 | 0.233 | 3.612
136 | 3 | window_2_0 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 0.743 | 1.92
137 | 3 | window_2_1 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 2.543 | 1.92
138 | 3 | window_2_2 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 4.343 | 1.92
139 | 3 | window_2_3 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 6.143 | 1.92
140 | 3 | window_2_4 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 7.943 | 1.92
141 | 3 | window_2_5 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 9.743 | 1.92
143 | 3 | window_3_0 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 0.482 | 1.92
144 | 3 | window_3_1 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 2.282 | 1.92
145 | 3 | window_3_2 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 4.082 | 1.92
146 | 3 | window_3_3 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 5.882 | 1.92
147 | 3 | window_3_4 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 7.682 | 1.92
148 | 3 | window_3_5 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 9.482 | 1.92
149 | 3 | window_3_6 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 11.282 | 1.92
150 | 3 | window_3_7 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 13.082 | 1.92
151 | 3 | window_3_8 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 14.882 | 1.92
152 | 3 | window_3_9 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 16.682 | 1.92
153 | 3 | window_3_10 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 18.482 | 1.92
154 | 3 | window_3_11 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 20.282 | 1.92
155 | 3 | window_3_12 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 22.082 | 1.92
156 | 3 | window_3_13 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 23.882 | 1.92
157 | 3 | window_3_14 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 25.682 | 1.92
159 | 3 | window_4_0 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 0.617 | 1.92
160 | 3 | window_4_1 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 2.417 | 1.92
161 | 3 | window_4_2 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 4.217 | 1.92
162 | 3 | window_4_3 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 6.017 | 1.92
163 | 3 | window_4_4 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 7.817 | 1.92
164 | 3 | window_4_5 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 9.617 | 1.92
166 | 3 | window_5_0 | window | wall_5 | E | -90 | 90 | 1.2 | 1.6 | 0.8 | 0.526 | 1.92
168 | 3 | window_6_0 | window | wall_6 | S | 0 | 90 | 1.2 | 3.01 | 0 | 0 | 3.612
170 | 3 | window_7_0 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 1.284 | 1.44
171 | 3 | window_7_1 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 4.884 | 1.44
172 | 3 | window_7_2 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 8.484 | 1.44
173 | 3 | window_7_3 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 12.084 | 1.44
174 | 3 | window_7_4 | window | wall_7 | E | -90 | 90 | 0.9 | 0.8 | 0.8 | 15.782 | 0.72
175 | 3 | window_7_5 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 19.375 | 1.44
179 | 4 | window_0_0 | window | wall_0 | N | 180 | 90 | 1.2 | 3.01 | 0 | 0.233 | 3.612
182 | 4 | window_2_0 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 0.743 | 1.92
183 | 4 | window_2_1 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 2.543 | 1.92
184 | 4 | window_2_2 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 4.343 | 1.92
185 | 4 | window_2_3 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 6.143 | 1.92
186 | 4 | window_2_4 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 7.943 | 1.92
187 | 4 | window_2_5 | window | wall_2 | N | 180 | 90 | 1.2 | 1.6 | 0.8 | 9.743 | 1.92
189 | 4 | window_3_0 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 0.482 | 1.92
190 | 4 | window_3_1 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 2.282 | 1.92
191 | 4 | window_3_2 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 4.082 | 1.92
192 | 4 | window_3_3 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 5.882 | 1.92
193 | 4 | window_3_4 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 7.682 | 1.92
194 | 4 | window_3_5 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 9.482 | 1.92
195 | 4 | window_3_6 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 11.282 | 1.92
196 | 4 | window_3_7 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 13.082 | 1.92
197 | 4 | window_3_8 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 14.882 | 1.92
198 | 4 | window_3_9 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 16.682 | 1.92
199 | 4 | window_3_10 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 18.482 | 1.92
200 | 4 | window_3_11 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 20.282 | 1.92
201 | 4 | window_3_12 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 22.082 | 1.92
202 | 4 | window_3_13 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 23.882 | 1.92
203 | 4 | window_3_14 | window | wall_3 | W | 90 | 90 | 1.2 | 1.6 | 0.8 | 25.682 | 1.92
205 | 4 | window_4_0 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 0.617 | 1.92
206 | 4 | window_4_1 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 2.417 | 1.92
207 | 4 | window_4_2 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 4.217 | 1.92
208 | 4 | window_4_3 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 6.017 | 1.92
209 | 4 | window_4_4 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 7.817 | 1.92
210 | 4 | window_4_5 | window | wall_4 | S | 0 | 90 | 1.2 | 1.6 | 0.8 | 9.617 | 1.92
212 | 4 | window_5_0 | window | wall_5 | E | -90 | 90 | 1.2 | 1.6 | 0.8 | 0.526 | 1.92
214 | 4 | window_6_0 | window | wall_6 | S | 0 | 90 | 1.2 | 3.01 | 0 | 0 | 3.612
216 | 4 | window_7_0 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 1.284 | 1.44
217 | 4 | window_7_1 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 4.884 | 1.44
218 | 4 | window_7_2 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 8.484 | 1.44
219 | 4 | window_7_3 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 12.084 | 1.44
220 | 4 | window_7_4 | window | wall_7 | E | -90 | 90 | 0.9 | 0.8 | 0.8 | 15.782 | 0.72
221 | 4 | window_7_5 | window | wall_7 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 19.375 | 1.44
225 | 5 | window_0_0 | window | wall_0 | W | 90 | 90 | 22 | 3.01 | 0 | 0.232 | 66.22
227 | 5 | window_1_0 | window | wall_1 | S | 0 | 90 | 11.4 | 3.01 | 0 | 0.094 | 34.314
229 | 5 | window_2_0 | window | wall_2 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 1.235 | 1.44
230 | 5 | window_2_1 | window | wall_2 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 4.835 | 1.44
231 | 5 | window_2_2 | window | wall_2 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 8.435 | 1.44
232 | 5 | window_2_3 | window | wall_2 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 12.035 | 1.44
233 | 5 | window_2_4 | window | wall_2 | E | -90 | 90 | 0.9 | 0.8 | 0.8 | 15.725 | 0.72
234 | 5 | window_2_5 | window | wall_2 | E | -90 | 90 | 1.8 | 0.8 | 0.8 | 19.343 | 1.44
236 | 5 | window_3_0 | window | wall_3 | N | 180 | 90 | 11.4 | 3.01 | 0 | 0.389 | 34.314

## ventilation_data
floor_number | area_floor_m2 | ceiling_height_m | vol_int_m3 | q_su_m3h | q_ex_m3h | q_inf_m3h | q_infadd_m3h | q_gap_m3h | epsilon_rec | t_in_star | f_temp_v | H_V_su | H_V_ie | H_V
0 | 347.82 | 3.01 | 1046.94 | 1565.19 | 1565.19 | 104.69 | 0 | 0 | 0.8 | 20 | 1 | 104.35 | 34.9 | 139.24
1 | 349.98 | 3.01 | 1053.45 | 1574.93 | 1574.93 | 105.35 | 0 | 0 | 0.8 | 20 | 1 | 105 | 35.12 | 140.11
2 | 349.98 | 3.01 | 1053.45 | 1574.93 | 1574.93 | 105.35 | 0 | 0 | 0.8 | 20 | 1 | 105 | 35.12 | 140.11
3 | 349.98 | 3.01 | 1053.45 | 1574.93 | 1574.93 | 105.35 | 0 | 0 | 0.8 | 20 | 1 | 105 | 35.12 | 140.11
4 | 349.98 | 3.01 | 1053.45 | 1574.93 | 1574.93 | 105.35 | 0 | 0 | 0.8 | 20 | 1 | 105 | 35.12 | 140.11
5 | 266.36 | 3.01 | 801.76 | 1198.64 | 1198.64 | 80.18 | 0 | 0 | 0.8 | 20 | 1 | 79.91 | 26.73 | 106.63

## walls_types
wall_type | thickness [m] | conductive resistance [m²K/W]
floor_ext | 0.47 | 0.24
floor_gr | 0.47 | 2.01
floor_sep_i | 0.42 | 2.12
floor_sep_u | 0.42 | 2.69
roof | 0.6 | 11.67
roof_terrace | 0.5 | 7.82
transom | 0.11 | 2.97
wall_ext | 0.29 | 3.99
wall_sep | 0.19 | 0.14

## walls
| floor_number | type | azimuth_deg | slope_deg | wall_type | area [m²] | f_temp | U [W/m²K] | H_T [W/K] | PHI_T [W]
0 | 0 | wall | -90 | 90 | wall_ext | 6.04 | 1 | 0.24 | 1.5 | 42
1 | 0 | wall | 180 | 90 | wall_ext | 24.81 | 1 | 0.24 | 6.4 | 172
2 | 0 | wall | 90 | 90 | wall_ext | 66.28 | 1 | 0.24 | 17 | 458
3 | 0 | wall | 0 | 90 | wall_ext | 28.93 | 1 | 0.24 | 7.4 | 200
4 | 0 | wall | -90 | 90 | wall_ext | 10.53 | 1 | 0.24 | 2.7 | 73
5 | 0 | wall | 0 | 90 | wall_ext | 0.98 | 1 | 0.24 | 0.3 | 7
6 | 0 | wall | -90 | 90 | wall_ext | 9.74 | 1 | 0.24 | 2.5 | 67
7 | 0 | wall | 180 | 90 | wall_ext | 4.41 | 1 | 0.24 | 1.1 | 30
8 | 1 | wall | 180 | 90 | wall_ext | 0.96 | 1 | 0.24 | 0.2 | 7
9 | 1 | wall | -90 | 90 | wall_ext | 6.53 | 1 | 0.24 | 1.7 | 45
10 | 1 | wall | 180 | 90 | wall_ext | 28.64 | 1 | 0.24 | 7.3 | 198
11 | 1 | wall | 90 | 90 | wall_ext | 66.05 | 1 | 0.24 | 16.9 | 457
12 | 1 | wall | 0 | 90 | wall_ext | 28.32 | 1 | 0.24 | 7.3 | 196
13 | 1 | wall | -90 | 90 | wall_ext | 10.38 | 1 | 0.24 | 2.7 | 72
14 | 1 | wall | 0 | 90 | wall_ext | 0.96 | 1 | 0.24 | 0.2 | 7
15 | 1 | wall | -90 | 90 | wall_ext | 72.57 | 1 | 0.24 | 18.6 | 502
16 | 2 | wall | 180 | 90 | wall_ext | 0.89 | 1 | 0.24 | 0.2 | 6
17 | 2 | wall | -90 | 90 | wall_ext | 6.07 | 1 | 0.24 | 1.6 | 42
18 | 2 | wall | 180 | 90 | wall_ext | 26.65 | 1 | 0.24 | 6.8 | 184
19 | 2 | wall | 90 | 90 | wall_ext | 61.45 | 1 | 0.24 | 15.7 | 425
20 | 2 | wall | 0 | 90 | wall_ext | 26.34 | 1 | 0.24 | 6.7 | 182
21 | 2 | wall | -90 | 90 | wall_ext | 9.66 | 1 | 0.24 | 2.5 | 67
22 | 2 | wall | 0 | 90 | wall_ext | 0.89 | 1 | 0.24 | 0.2 | 6
23 | 2 | wall | -90 | 90 | wall_ext | 67.51 | 1 | 0.24 | 17.3 | 467
24 | 3 | wall | 180 | 90 | wall_ext | 0.89 | 1 | 0.24 | 0.2 | 6
25 | 3 | wall | -90 | 90 | wall_ext | 6.07 | 1 | 0.24 | 1.6 | 42
26 | 3 | wall | 180 | 90 | wall_ext | 26.65 | 1 | 0.24 | 6.8 | 184
27 | 3 | wall | 90 | 90 | wall_ext | 61.45 | 1 | 0.24 | 15.7 | 425
28 | 3 | wall | 0 | 90 | wall_ext | 26.34 | 1 | 0.24 | 6.7 | 182
29 | 3 | wall | -90 | 90 | wall_ext | 9.66 | 1 | 0.24 | 2.5 | 67
30 | 3 | wall | 0 | 90 | wall_ext | 0.89 | 1 | 0.24 | 0.2 | 6
31 | 3 | wall | -90 | 90 | wall_ext | 67.51 | 1 | 0.24 | 17.3 | 467
32 | 4 | wall | 180 | 90 | wall_ext | 0.96 | 1 | 0.24 | 0.2 | 7
33 | 4 | wall | -90 | 90 | wall_ext | 6.58 | 1 | 0.24 | 1.7 | 46
34 | 4 | wall | 180 | 90 | wall_ext | 28.88 | 1 | 0.24 | 7.4 | 200
35 | 4 | wall | 90 | 90 | wall_ext | 66.59 | 1 | 0.24 | 17.1 | 460
36 | 4 | wall | 0 | 90 | wall_ext | 28.55 | 1 | 0.24 | 7.3 | 197
37 | 4 | wall | -90 | 90 | wall_ext | 10.46 | 1 | 0.24 | 2.7 | 72
38 | 4 | wall | 0 | 90 | wall_ext | 0.96 | 1 | 0.24 | 0.2 | 7
39 | 4 | wall | -90 | 90 | wall_ext | 73.16 | 1 | 0.24 | 18.7 | 506
40 | 5 | wall | 90 | 90 | wall_ext | 1.4 | 1 | 0.24 | 0.4 | 10
41 | 5 | wall | 0 | 90 | wall_ext | 1.94 | 1 | 0.24 | 0.5 | 13
42 | 5 | wall | -90 | 90 | wall_ext | 75.74 | 1 | 0.24 | 19.4 | 524
43 | 5 | wall | 180 | 90 | wall_ext | 1.79 | 1 | 0.24 | 0.5 | 12
44 | 0 | panel | -90 | 90 | wall_sep | 11.22 | 0.74074 | 3.24 | 27 | 728
45 | 0 | panel | -90 | 90 | transom | 8.25 | 1 | 0.32 | 2.8 | 75
46 | 0 | roof | 0 | 180 | floor_sep_u | 347.82 | 0 | 0.35 | 0 | 0
47 | 1 | floor | 0 | 0 | floor_sep_u | 347.82 | 0 | 0.35 | 0 | 0
48 | 1 | roof | 0 | 180 | floor_sep_i | 349.98 | 0 | 0.44 | 0 | 0
49 | 2 | floor | 0 | 0 | floor_sep_i | 349.98 | 0 | 0.44 | 0 | 0
50 | 2 | roof | 0 | 180 | floor_sep_i | 349.98 | 0 | 0.44 | 0 | 0
51 | 3 | floor | 0 | 0 | floor_sep_i | 349.98 | 0 | 0.44 | 0 | 0
52 | 3 | roof | 0 | 180 | floor_sep_u | 349.98 | 0 | 0.35 | 0 | 0
53 | 4 | floor | 0 | 0 | floor_sep_u | 349.98 | 0 | 0.35 | 0 | 0
54 | 4 | roof | 0 | 180 | floor_sep_i | 266.36 | 0 | 0.44 | 0 | 0
55 | 5 | floor | 0 | 0 | floor_sep_i | 266.36 | 0 | 0.44 | 0 | 0
56 | 0 | floor | 0 | 0 | floor_gr | 347.82 | 0.37037 | 0.46 | 98.6 | 2661
57 | 1 | floor | 0 | 0 | floor_ext | 2.16 | 1 | 2.45 | 5.3 | 144
58 | 4 | roof | 0 | 180 | roof_terrace | 83.62 | 1 | 0.13 | 12.1 | 328
59 | 5 | roof | 0 | 180 | roof | 266.36 | 1 | 0.08 | 27.8 | 751
0 | 0 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
1 | 0 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
2 | 0 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
3 | 0 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
4 | 0 | window | 180 | 90 | window | 7.2 | 1 | 1.05 | 7.7 | 208
5 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
6 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
7 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
8 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
9 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
10 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
11 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
12 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
13 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
14 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
15 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
16 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
17 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
18 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
19 | 0 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
20 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
21 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
22 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
23 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
24 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
25 | 0 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
26 | 0 | window | -90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
27 | 0 | window | 0 | 90 | window | 2.4 | 1 | 1.05 | 2.6 | 69
28 | 0 | window | -90 | 90 | window | 39.6 | 1 | 1.05 | 42.4 | 1144
29 | 1 | window | 180 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
30 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
31 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
32 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
33 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
34 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
35 | 1 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
36 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
37 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
38 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
39 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
40 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
41 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
42 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
43 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
44 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
45 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
46 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
47 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
48 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
49 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
50 | 1 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
51 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
52 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
53 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
54 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
55 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
56 | 1 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
57 | 1 | window | -90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
58 | 1 | window | 0 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
59 | 1 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
60 | 1 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
61 | 1 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
62 | 1 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
63 | 1 | window | -90 | 90 | window | 0.72 | 1 | 1.05 | 0.8 | 21
64 | 1 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
65 | 2 | window | 180 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
66 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
67 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
68 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
69 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
70 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
71 | 2 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
72 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
73 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
74 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
75 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
76 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
77 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
78 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
79 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
80 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
81 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
82 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
83 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
84 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
85 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
86 | 2 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
87 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
88 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
89 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
90 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
91 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
92 | 2 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
93 | 2 | window | -90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
94 | 2 | window | 0 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
95 | 2 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
96 | 2 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
97 | 2 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
98 | 2 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
99 | 2 | window | -90 | 90 | window | 0.72 | 1 | 1.05 | 0.8 | 21
100 | 2 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
101 | 3 | window | 180 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
102 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
103 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
104 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
105 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
106 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
107 | 3 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
108 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
109 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
110 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
111 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
112 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
113 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
114 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
115 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
116 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
117 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
118 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
119 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
120 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
121 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
122 | 3 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
123 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
124 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
125 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
126 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
127 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
128 | 3 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
129 | 3 | window | -90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
130 | 3 | window | 0 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
131 | 3 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
132 | 3 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
133 | 3 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
134 | 3 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
135 | 3 | window | -90 | 90 | window | 0.72 | 1 | 1.05 | 0.8 | 21
136 | 3 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
137 | 4 | window | 180 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
138 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
139 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
140 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
141 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
142 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
143 | 4 | window | 180 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
144 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
145 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
146 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
147 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
148 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
149 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
150 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
151 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
152 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
153 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
154 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
155 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
156 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
157 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
158 | 4 | window | 90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
159 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
160 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
161 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
162 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
163 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
164 | 4 | window | 0 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
165 | 4 | window | -90 | 90 | window | 1.92 | 1 | 1.05 | 2.1 | 55
166 | 4 | window | 0 | 90 | window | 3.61 | 1 | 1.05 | 3.9 | 104
167 | 4 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
168 | 4 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
169 | 4 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
170 | 4 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
171 | 4 | window | -90 | 90 | window | 0.72 | 1 | 1.05 | 0.8 | 21
172 | 4 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
173 | 5 | window | 90 | 90 | window | 66.22 | 1 | 1.05 | 70.9 | 1913
174 | 5 | window | 0 | 90 | window | 34.31 | 1 | 1.05 | 36.7 | 991
175 | 5 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
176 | 5 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
177 | 5 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
178 | 5 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
179 | 5 | window | -90 | 90 | window | 0.72 | 1 | 1.05 | 0.8 | 21
180 | 5 | window | -90 | 90 | window | 1.44 | 1 | 1.05 | 1.5 | 42
181 | 5 | window | 180 | 90 | window | 34.31 | 1 | 1.05 | 36.7 | 991

## TR_by_walls_types_zone
floor_number | wall_type | area [m²] | H_T [W/K] | PHI_T [W]
0 | floor_gr | 347.82 | 98.6 | 2661
0 | floor_sep_u | 347.82 | 0 | 0
0 | transom | 8.25 | 2.8 | 75
0 | wall_ext | 151.72 | 38.9 | 1049
0 | wall_sep | 11.22 | 27 | 728
0 | window | 99.12 | 106.1 | 2864
1 | floor_ext | 2.16 | 5.3 | 144
1 | floor_sep_i | 349.98 | 0 | 0
1 | floor_sep_u | 347.82 | 0 | 0
1 | wall_ext | 214.41 | 54.9 | 1482
1 | window | 68.9 | 73.7 | 1991
2 | floor_sep_i | 699.97 | 0 | 0
2 | wall_ext | 199.46 | 51.1 | 1379
2 | window | 68.9 | 73.7 | 1991
3 | floor_sep_i | 349.98 | 0 | 0
3 | floor_sep_u | 349.98 | 0 | 0
3 | wall_ext | 199.46 | 51.1 | 1379
3 | window | 68.9 | 73.7 | 1991
4 | floor_sep_i | 266.36 | 0 | 0
4 | floor_sep_u | 349.98 | 0 | 0
4 | roof_terrace | 83.62 | 12.1 | 328
4 | wall_ext | 216.15 | 55.4 | 1495
4 | window | 68.9 | 73.7 | 1991
5 | floor_sep_i | 266.36 | 0 | 0
5 | roof | 266.36 | 27.8 | 751
5 | wall_ext | 80.87 | 20.7 | 559
5 | window | 142.77 | 152.8 | 4125

## TR_by_zone
floor_number | area_wv [m²] | area_wh [m²] | area_wd [m²] | area_T [m²] | H_T_wv [W/K] | H_T_wh [W/K] | H_T_wd [W/K] | H_T [W/K] | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W]
0 | 171.19 | 695.64 | 99.12 | 965.95 | 68.6 | 98.6 | 106.1 | 273.2 | 1853 | 2661 | 2864 | 7377
1 | 214.41 | 699.97 | 68.9 | 983.28 | 54.9 | 5.3 | 73.7 | 134 | 1482 | 144 | 1991 | 3617
2 | 199.46 | 699.97 | 68.9 | 968.33 | 51.1 | 0 | 73.7 | 124.8 | 1379 | 0 | 1991 | 3370
3 | 199.46 | 699.97 | 68.9 | 968.33 | 51.1 | 0 | 73.7 | 124.8 | 1379 | 0 | 1991 | 3370
4 | 216.15 | 699.97 | 68.9 | 985.03 | 55.4 | 12.1 | 73.7 | 141.2 | 1495 | 328 | 1991 | 3813
5 | 80.87 | 532.73 | 142.77 | 756.37 | 20.7 | 27.8 | 152.8 | 201.3 | 559 | 751 | 4125 | 5435

## PHI_by_zone
floor_number | PHI_T_wv [W] | PHI_T_wh [W] | PHI_T_wd [W] | PHI_T [W] | PHI_V_su [W] | PHI_V_ie [W] | PHI_V [W] | PHI_TOT [W] | PHI_RH [W] | PHI_HL [W]
0 | 1853 | 2661 | 2864 | 7377 | 2817 | 942 | 3760 | 11137 | 3478 | 14615
1 | 1482 | 144 | 1991 | 3617 | 2835 | 948 | 3783 | 7400 | 3500 | 10900
2 | 1379 | 0 | 1991 | 3370 | 2835 | 948 | 3783 | 7153 | 3500 | 10653
3 | 1379 | 0 | 1991 | 3370 | 2835 | 948 | 3783 | 7153 | 3500 | 10653
4 | 1495 | 328 | 1991 | 3813 | 2835 | 948 | 3783 | 7596 | 3500 | 11096
5 | 559 | 751 | 4125 | 5435 | 2158 | 722 | 2879 | 8314 | 2664 | 10978

## PHI_by_facade
azimuth_deg | PHI_TOT [W] | PHI_HL [W]
-90 | 15343 | 22346
0 | 8229 | 11427
90 | 16899 | 23625
180 | 8281 | 11496